# page_17.png

UNCERTAINTY ANALYSIS OF GAS METERING SYSTEM

PM4 POWER PLANT

3.0 ULTRASONIC METER UNCERTAINTY

1

Pressure al linc condition. bar a

1

Prcssurc at basc condition; 1,01325 bar a

T,

Tcmperalurc at line condition; %C'

T;

'Temperalure at basc condition; 15 %C (288,15 K)

Z,

Gas compressibility at line condition; calculated in accordancc wilh AGA 8-1994

Z,

Gas compressibility at basc condition; calculalcd in accordance witl IS0 6976-1995

p

Gas density al linc condition; calculated in accordancc will AGA 8 - 1994

0l

Gas density at base condition, calculated in accordancc with IS0 6976-1995

3.3 Derivation of ultrasonic metering uncertainty

The  ultrasonic  tnelcr

was senl lor

2

wet  calibration at

a third party calibration facility in

C'EESI. From thc calibralion certificale; CILSI had dcclared that Ile mnaximum tolerance crror of

the calibrated mcter is (,064 % for FT 1420. 0,05 % lor FT 1440.

From the

experimcntal rcsult ol the calibration; the maximum calibration uncertainty (Ucal) of

melers which will allcct the actual mncasurcmnent during opcralion is estimated for this experimental

dala 0,18 % ol calibrated span.

An installation conliguration error will contributed to the meter installalion at site

(Umi).

9 Section 7.2.2. recommended that a maximun error is 0,3 % lor this effect and it has accounted for

the k multiplicr .

Thne USM combined uncertainty is givcn a lollow

cul

Uol

mi

U(m) =

2

1,73

2,45

Thic calculated cxpandcd unccrtainty lor ultrasonic meter is summarized in tables below

For FT _ 1420

Ultrasonic meter

Standard uncertainty (% "

Combined

Expanded

flow rangc (%)

uncertainty

uncertainty

Utol

Umi

k = 2

5,0

0,15

o,000

0,30

0,14

0,29

10,!

017

u,uuo

0,30

0,15

0,30

25,2

0,217

@,u0o

0,30

0215

0,30

39,9

0,15

@,000

",30

014

0,29

69,8

0,14

(),uo0

0,30

044

(,28

80,4

015

Q,uou

0,30

0,14

0,29

ci

1,(0

1,00

1,00

Pngc 7 0f31

Ucal