## Page: page_26.png

| Uadc | =+ | 0,01 % of reading for TT | 1424 |
| --- | --- | --- | --- |
| Utadc | =+ | 0,01 % of reading for TT | 1444 |

| Uudlac | Digital accuracy_ | 0,500 | Rectangular | 1,73 | 1,00 | 0,289 | 8,35E-02 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Uudu | DIA_Accuracy | 0,080 | Rectangular | 1,73 | 1,00 | 0,046 | 2,14E-03 |

| Uuol | tolerance | 0,/90 | Rectangular | 1,73 | 1,00 | 02110 | 1,20E-02 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Uu | Drift | 0,050 | Rectangular | 1,73 | 1,00 | 0,029 | 8,33E-04 |

UNCERTAINTY ANALYSIS OF GAS METERING SYSTEM ~ PM4 POWER PLANT

4.0 STANDARD VOLUME FLOWRATE UNCERTAINTY

Utp 4 0,18% of reading

when calculating the slandard uncertainty a rectangle distribution is assumed with a coverage

factor k = 1,73 .

4.1.2.8 ADC tolerance

padlc

The analogue to digital converter at the input of the {low computer is checked by routine

calibration to be within the tolerance of + 0,1% of span. However the Uudac < after calibration is:

When calculating the standard   uncertainty a rectangular   distribution is assumed with a

coverage factor k = 1,73 .

4.1.2.9 Combined uncertainty

The combined standard uncertainty calculaled using the equation

Adac: teal llemp Itul Jaudlc

U, +(%;(

2

is represented in a tabular form as shown below, note that the sensitivity coefficient c; lor each

input is 1 as they are all expressed as a percentage ot the lemperature reading.

For TT _ 1424

Source Value

Symbol Distribution Divisor Ci Ili (c; X v;)?

of Uncertainty

Ucal Transmitter calibration 0,700 Normal 2,00 1,00 0,350 1,23E-01

Uuenp Ambient temperature effect 0,050 Rectangular 1,73 1,00 0,029 8,336-04

Transmitter calibration

Uw Power supply effect 0,100 Rectangular 1.73 1,00 0,058 3,33E-03

Uladc ADC test 0,040 Rectangular 1,73 1,00 0,023 5,331-04

U() Combined standard_uncertainty Normal 0,475

Uo Fxpanded uncertainty Normal (k=2) 2,00 0,95

Page 16 of 31