## Page: page_28.png

| calg | Calibration gas uncertainty |
| --- | --- |
| Utol | 'The calibration tolerance |

| C | 0,8880 | 0,0236 | u01 | 0,02 | 0,0336 | 0,90386! |
| --- | --- | --- | --- | --- | --- | --- |
| N | ',0048 | 0,3506 | 0,06 | 0,02 | 0,3584 | 0,007561 |

UNCERTAINTY ANALYSIS OF GAS METERING SYSTEM PM4 POWER PLANT

4.0 STANDARD VOLUME FLOWRATE UNCERTAINTY

where the sources of uncertainty are taken to be

Uculg the uncertainty in the calibration gas

Utol The tolerance applied during the calibration

Urep the repeatability of the measurement

The upstream density is calculated from the gas composition measured by a

gas

chromatograph, the   sensitivity   coellicients for   each of the input   quantities are calculated  by

successively increasing and decreasing each input by the magnitude of its estimated uncertainty and

calculating the elfect this has on the resulting density as described in the GUM'

temporary variable Zi is first calculated

Z; = [f(n_ + u(x,)_,x,) - f ((xv",x; = u(x,),x))]

and where the expanded uncertainty is expressed in the form:

N

u, (y) = 2c .uỉ (x,)

1~

the value of each sensitivity coefficient c; taken as Z/u(xi).

4.1.3.1 Sensitivity coefficients for upstream density uncertainty

The uncertainty calculation for each component and the sensitivity coefficients are shown in

the table below

The combined standard uncerlainty for each component is calculated by:

calg tol rep

u m :=

Where the sources of uncertainty are taken to be:

Urcp The gas chromatograph repeatability

Sensitivity_coefficient calculation

Cal. gas Calibration Chromatograph Combined

Component

uncertainty tolerance repealability uncerlainty  C;

value

(%) (%) (%) (%)

Guide t0 the Expression of Uncertainty in Aleasuremen. Section J

Page 18 0l 31