## Page: page_30.png

| T | Line temperature | 0,969) | Normal | 2,00 | -0,09158 | 0,48 | 1,9742-03 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Z | Equalion ol state | 0, 1 00 | Normal | 2,00 | 1,(0006 | 0,05 | 2,50/;-03 |

| C | Methane | 0,034 | Norinal | 2,0() | (),90386 | 0,02 | 2,30E:-04 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| N | Nitrogen | 0,358 | Normal | 2,00 | (),00756 | 0,18 | 1,841,-06 |

| Cz | Ethane | 0,433 | Norna/ | 2,00 | 0,08757 | 0,22 | 3,6016-04 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| C | Propane | 0,313 | Normal | 2,(() | 0,06617 | 0,16 | 1,071;-04 |
| iCi | i-Butane | 0,358 | Normal | 2,00 | 0,02032 | 0,18 | 1,321-05 |
| nC4 | n-Butane | (),344 | Normal | 2,00 | (,01859 | 0,17 | 1,0218-05 |
| iCs | i-Pentane | 0,583 | Normal | 2,00 | 0,00778 | 0,29 | 5,141:-06 |
| nC5 | n-Pentane | 0,674 | Normal | 2,00 | (,00479 | 0,34 | 2,601-06 |
| nC6 | n-Hexane | 1,046 | Nornval | 2,(() | 0,00876 | 0,52 | 2,10E-05 |

UNCERTAINTY ANALYSIS OF GAS METERING SYSTEM = PMA POWER PLANT

4.0 STANDARD VOLUME FLOWRATE UNCERTAINTY

For FT- 1440

Source Value

Symhol Dislrihution Divisor U; (c; X u;)?

(f uncertainty

Absolute pressure (,/21 Nornnal 2,00 1,08993 0,06 4,32E-03

CO2 Carbon [ioxide 0,306 Normzal 2,0)0) 0,(6374 0,15 9,521;-05

UoRh) Combined slandard uncettainty Normal 0,098

U(hu) Expanded uncertainty Normal (k=2) 2,00 0,20

4.2 Standard density

The standard   density is calculated fron the gas composition measured by à gas

chromatograph.

'The functional relationship used to determine the standard density is defined in ISO 69765

1995. This can be wrillen in the lorn

y = f(x1, X2, X). _ Xi)

where the output y (slandard density ) is a lunction ola number of inputs x (components forming the

gas composition)

The sensitivity coelficients lor each ol the input quantities are calculated by the same finite

difference melhod as used wlven calculating the sensitivity coellicients for the upstream density .

4.2.1 Sensitivity coefficients for standard density uncertainty

The uncertainty calculation lor eacl component and the sensitivity coellicients are shown in

the table below

The combined standard uncertainty [or each component is calculated by

calg tol rep

U m :=

5

IS6) 6976 Nutural (ìas ( 'ulculalion 0f calowvifìc values; dlensily; relaive dlensity aul Wobbe inlex_fium t gas compusilion

Page 20 ol 31