## Page: page_38.png

| 5,0 | 250,31 | 8817,9 | 358578,0 | (,35 | 0,36 |
| --- | --- | --- | --- | --- | --- |
| 10,1 | 503,54 | 17738,8 | 721338,9 | (,36 | 0,37 |
| 25,2 | 1262,44 | 44473,4 | 1808490,1 | 0,36 | 0,37 |
| 39,9 | 1996,41 | 70329,7 | 2859928,2 | (,35 | 0,36 |
| 69,8 | 3488,23 | 122883,7 | 4997013,2 | (,34 | 0,36 |
| 80,4 | 4021,72 | 441677,6 | 5761256,6 | 0,35 | 0,36 |

0,80

2,60

UNCERTAINTY ANAIYSIS OF (AS METERING SYSTEM PM4 POWER PLANT

6.0 SUMMARY OF METERING SYSTEM UNCERTAINTY

This  section  provides tle summary results of the  uncerlainty   estimation lor each gas metering

system. The detail calculation has been performed based on [S05168- 2002 and shown in Appendix

A, B and € .

The uncerlainty estimation perlormed has been based on results described in the product catalogue;

results obtained from some analysis and results from some third party testing lacility

In summary, the uncerlainty estimation was witlin the project allowable limit. Tle sumnary result

was indicaled as below

For FQI _ 1420

'The maximun expanded uncerlainty for standard volume Ilow rate = 0,36 %

The maximun expanded uncertainty for energy (low rate = 0,37 %

% Flowrate Energy flowrate

Standard flowrale Uexp standard Ucxp energy flowrate

(1 '/h) (n1' /h) *) flowrale (%) (%)

Iax (MJIl)

8 The unit of volume flowvate is converted t0 the reference conlition at 1,01325 bu < and 15 "'

Standard Flowrate Expanded Uncertainty

0,35 036

0,36 0,85

0,3

E ,20

,00

5 5,01 10,07 25,25 39,93 69,76 80,43

% of Qmax

Page 28 0l3